# ANNEX II + III:	 TECHNICAL SPECIFICATIONS + TECHNICAL OFFER

# Contract title: Supply of equipment – EV Chargers	p 1 /…

Publication reference: G4G - 24258 – 04

Columns 1-2 should be completed by the contracting authority

Columns 3-4 should be completed by the tenderer

Column 5 is reserved for the evaluation committee

Annex III - the contractor's technical offer

The tenderers are requested to complete the template on the next pages:

- Column 2 is completed by the contracting authority shows the required specifications (not to be modified by the tenderer),

- Column 3 is to be filled in by the tenderer and must detail what is offered (for example the words ‘compliant’ or ‘yes’ are not sufficient)

- Column 4 allows the tenderer to make comments on its proposed supply and to make eventual references to the documentation

The eventual documentation supplied should clearly indicate (highlight, mark) the models offered and the options included, if any, so that the evaluators can see the exact configuration. Offers that do not permit to identify precisely the models and the specifications may be rejected by the evaluation committee.

The offer must be clear enough to allow the evaluators to make an easy comparison between the requested specifications and the offered specifications.

The tenderer is expected to submit documentary evidence (brochures, technical data sheets etc.) of the technical compliance of his offer.

In addition to the supply of the electric vehicle charging stations, the Contractor shall include in its offer all ancillary activities and services necessary for the complete, safe, and operational installation of the chargers at the designated locations.

These activities shall be considered incidental and subordinate to the supply and shall form an integral part of the Contractor’s scope of supply.

The Contractor shall ensure that all installation-related activities are carried out in accordance with:

- Applicable national legislation

- Relevant technical standards and regulations

- Safety requirements

- Good engineering practice

The Contractor shall be deemed to have reviewed all available documentation and assessed the conditions for installation. All costs related to the execution of these activities shall be included in the financial offer, including: Materials, Transport, Labour, Equipment, Testing and commissioning, Documentation.

No separate measurement or payment shall be made for installation-related activities.

The installation shall be considered complete only when:

- The charging stations are fully installed and operational

- All systems are tested and commissioned

- All required documentation has been submitted

| 1. Item number | 2. Specifications required | 3. Specifications offered | 4. Notes, remarks, ref to documentation | 5. Evaluation committee’s notes |
| --- | --- | --- | --- | --- |
| 1 | Fast DC Chargers in Municipality of Strumica, Radovish, Novo Selo, Gevgelija, Dojran and Valandovo |  |  |  |
|  | Quantity: 6 |  |  |  |
|  | Manufacturer’s name: |  |  |  |
|  | Product type, model: |  |  |  |
|  | Specifications: Procurement, transport, delivery, and installation of fast e-chargers and additional equipment on previously conducted activities and materials for their installations, including examinations and tests, commissioning, set up and training of the personnel, with the following specifications: DC Plug: - Charging method: Mod 4 - Output power: 150Kw ±10%, with modules of 30kW or 20kW each, and a reserve for future expansion of min. 2 modules - Output voltage: 150-950V - Output electricity: CCS2: 200-300A - Number of outputs: 2*CCS2 + 1*AC (optional) - Efficiency: ≥96% AC Plug: Grounding system: TNC-S, 3P+N+PE Input voltage: 3P, 400V AC±10% Input frequency: 50Hz Power factor (cosφ): ≥0.99 Harmonic Distortion: ≤5% |  |  |  |
|  | General features: - Housing protection type: IP54, IK10 - Material: ► Housing made of stainless steel, anodized aluminum or similar material with a high degree of anti-corrosion protection against atmospheric influences, ►screen protective glass made of tempered glass with a high degree of mechanical impact - Working altitude: 2000m - Operating temperature: -35℃~+75℃ - Installation method: On the ground (foundation-according to variants given in the construction and architectural part) - Approximate dimensions (HxWxD): According to the spatial conditions given in graphic attachments User interface: - Type of screen (monitor): LED touch from min. 10.1 inches - Cable length: min. 5 meters - Charging status indicator: - LED/LCD/APP - User interface: APP; Cloud - Communication: 4G, Wi-Fi, Ethernet - Communication protocol: OCCP 1.6 with the possibility of expansion to 2.1 - User authorization: APP, RFID card, Payment card Safety standards: - Safety and compliance: IEC 61851-1; IEC 61851-23; IEC 61851-21-2; ISO 15118 Plug&Charge - Certification and standards: CE, EMC Class A - Warranty: min. 24 months |  |  |  |
|  | Management system As part of the procurement and delivery of the e-charger, the contractor/supplier is obliged to provide a management system for its management. The management system should be based on a "cloud based" cloud, which will enable remote access to the Investor via the Internet "web based" (web app & backend portal) and web application The system should enable at least the following functionalities: - Remote control and real-time monitoring of the overall operation of the e-charger (parameters, statuses, etc.) and their archiving - Diagnostics of the hardware of the e-charger (hardware-agnostic) - Possibility of expansion with new locations and chargers - API basis for its modification and expansion according to the requirements of the Investor - Operational and internet security security and its remote advancement (update) - Possibility of the so-called "White labeling" ie personification of the Investor's requirements - Setting fixed and dynamic tariff prices for services - Possibility of its expansion (Scalability) |  |  |  |
|  | - Automatic and on-demand error diagnostics - Entering, determining and controlling tariff models for electricity and other tariff / promotional models that will enable optimal use (exploitation) of chargers - Roaming, i.e. the ability to connect to other platforms/chargers from different entities - the possibility of connecting other systems and equipment, including video surveillance As part of the Management system, it is necessary to contain at least the following modules: - User registration module - Module for operational work - Billing module - Reports and analytics module Grounding: Procurement, transportation and execution of a grounding device with a ferro-galvanized conductor with a thickness of Ф10mm and a length of 9m, placed at a depth of 60cm from the ground, complete with compaction of stepped probes with a thickness of Ф22mm and a length of min. 3 m, including construction works of excavation and re-burying - 1 complete set |  |  |  |
|  | Supply, transport and execution of lightning arrester installation, complete with arrester, clips for steel profiles with highly insulated conductor and gutter clamps with highly insulated conductor - 1 complete set Procurement, transport and installation of highly insulated conductor – 8 metres Equalization of the potential in the distribution cabinet and the e-charger with all metal parts of the station - 1 complete set Cabinets: Procurement, transport and installation of a free-standing distribution cabinet (1 complete set) made of double-pickled sheet metal with a thickness of min. 2mm, complete with a concrete base and a rubber mat for protection against reptiles, with a degree of protection of IP54 and equipped with the following equipment: - Automatic assembly 300A/3P x 1 piece - Automatic assembly 300A/3P x 1 piece - Automatic fuses 6A/1P x 2 pieces - System for automatic astronomical lighting of lamps (trout and astronomical clock, complete with contactors, assemblies and light) - Internet router with integrated WiFi, switch with min. 3 ports and speed of min. 300mbps - Remaining joined material - Single-pole closet pattern |  |  |  |
|  | Cables and accessories: Procurement, transportation and installation of energy cable type NA2X2Y 2x4x(1x240) mm², 1kV – 5 meters Supply, transport and installation of power cable type NYY 3x1.5 mm² - 30 meters Procurement, transport and installation of CAT7 power cable – 10 meters Procurement, transport and installation of LED lights (led tracks) in green color, complete with aluminum superstructure profiles for mounting led tracks with IP54 degree of protection and mechanical resistance of IK 08 – 5,2 meters Procurement, transport and installation of LED lamps (led tracks) in warm white color (4000K) power of 12W, complete with aluminum superstructure profiles for mounting led tracks with IP54 degree of protection and mechanical resistance of IK 08 – 10 meters Procurement, transport and installation of LED lamps (led tracks) in green color or color of the investor's choice, power of 12W, complete with aluminum superstructure profiles for mounting led tracks with IP54 degree of protection and mechanical resistance of IK 08 – 5 meters |  |  |  |
|  | Procurement, transport and installation of a Megapixel Day/Night IP camera (1 piece) with built-in IP lighting with the following features: - 2.8" progressive CMOS sensor - Up to 2.0 megapixels - 2.8mm/4mm/6mm fixed focal lenses - From a minimum of 10 m. IR range. - Double flow, - Digital WDR (Wide Dynamic Range) - 3D DNR (Digital Noise Reduction) - PoE (Power over Internet) - IP67, IK10 - Remote monitoring of the station - the possibility of accessing the camera (visual insight) through the web portal and the management system, as well as the possibility of automatic detection of movement/charging within the station and recording and storage of the video material. Examination and tests: Examination of the correctness of the installation - 1 complete set Measurement of touch resistance and issuance of a certificate by an accredited company - 1 complete set Measurement of the resistance of the earthing conductor and issuance of a certificate by an accredited company - 1 complete set Preparation of as-built documentation - 1 complete set |  |  |  |
|  | Activities and materials for installation of fast chargers (architectural, civil and traffic): Site Preparation and Removal Works The Contractor shall perform all necessary site preparation and surface adjustment activities required for the installation of the charging stations. This shall include: - Removal of existing surface elements (e.g. paving, tiles, or similar structures) where required - Handling, loading, transport, and disposal of removed materials in accordance with applicable regulations Site preparation activities shall be limited to what is necessary for installation and shall be included in the Contractor’s scope of supply. The Contractor shall carry out all necessary ground preparation and excavation activities required for the installation of the equipment and supporting structures. This shall include: - Marking and positioning of installation points based on provided drawings - Excavation and preparation of the installation area - Handling and disposal of excavated material All excavation and ground preparation shall be considered incidental to the installation of the supplied equipment. |  |  |  |
|  | Foundation and Base Structure The Contractor shall provide suitable foundation and base structures required for the safe and stable installation of the charging stations. This shall include: - Construction of a base/foundation plate - Preparation of mounting surface - Alignment and leveling Indicative Requirements: - The foundation may include a base plate with approximate dimensions of 160 × 280 x 50 - A pedestal for mounting the charger may be required with approximate dimensions of 70 × 80 x 15 Technical Requirements: - Foundations shall ensure structural stability and durability - Materials shall be suitable for outdoor use and load-bearing conditions Foundations shall be considered part of the installation necessary for the operation of the supplied equipment. Reinforcement Elements (within Foundation Structures) The Contractor shall include all necessary reinforcement elements required for the structural integrity and durability of the foundation and supporting structures of the charging stations. This shall include: - Supply, preparation, and installation of reinforcement materials - Cutting, shaping, and placement within the foundation structures - Integration with formwork and concrete elements |  |  |  |
|  | Technical Requirements: - Reinforcement steel shall be of appropriate grade (e.g. B500 or equivalent) - Dimensions and configuration shall be suitable for the intended structural function - Installation shall ensure stability, durability, and load-bearing capacity Reinforcement elements shall be considered part of the foundation system and included in the Contractor’s scope of supply Steel Structure and Protective Canopy The Contractor shall supply and install a prefabricated steel structure forming a protective canopy for the EV charging stations. The canopy shall be delivered as a complete system, including all structural and functional components required for its stability and operation. This shall include, but is not limited to: - Vertical and inclined steel support elements (pillars/columns) - Main load-bearing beams and structural profiles - Roof supporting substructure - Fixing and connection elements (bolts, anchors, fasteners) - Water drainage elements, including horizontal and vertical gutters - Base plates and connection interfaces to the foundation - All necessary accessories for full assembly and installation |  |  |  |
|  | Technical Requirements - The structure shall be made of structural steel profiles suitable for outdoor use - Steel elements shall be: - Corrosion-protected (e.g. galvanized or equivalent) - Resistant to environmental conditions and mechanical loads - The canopy shall: - Provide adequate protection from weather conditions - Ensure structural stability under operational loads - Be compatible with the charger layout and positioning The configuration, geometry, and approximate dimensions of the steel structure are defined in the technical documentation and graphic attachments provided with the tender dossier. Tenderers shall use these drawings as a basis for: • Understanding the structure layout • Estimating material quantities • Preparing their financial offer |  |  |  |
|  | Auxiliary Metal (Locksmith) Elements The Contractor shall supply and install all necessary auxiliary metal elements required for the proper functioning, safety, and completion of the canopy system. Scope of Supply This shall include: - Protective and safety elements (e.g. posts, guards, or similar components) - Fixing plates and connection elements - Fasteners and anchoring systems - Informational or signage panels integrated into the structure Technical Requirements • All elements shall be made of durable metal materials suitable for outdoor use • Surfaces shall be: o Corrosion-protected o مقاust to environmental conditions • Informational panels shall: o Be clearly visible o Include required markings and identification All auxiliary elements shall be included in the Contractor’s scope of supply. Protective Coatings and Surface Treatment The Contractor shall apply all necessary protective coatings and treatments required to ensure durability and proper functioning of the installation. This shall include: - Waterproofing of foundation and exposed surfaces - Protective coatings for metal elements - Surface treatment at connection interfaces between steel and concrete |  |  |  |
|  | Technical Requirements - Materials shall be: - Suitable for outdoor conditions - Resistant to moisture and environmental exposure - Application shall ensure: - Long-term protection - Proper adhesion and coverage Protective treatments shall be included as part of the installation necessary for the operation of the supplied system. Site Reinstatement and Finishing Works The Contractor shall restore all affected areas to their original or equivalent condition after installation. This shall include: - Reinstatement of paving or surface elements - Adjustment of surrounding areas affected by installation - Finishing works necessary for proper integration into the existing environment Site reinstatement shall be limited to areas affected by installation and included in the Contractor’s scope of supply. Traffic Marking and Signage The Contractor shall provide and install all necessary traffic marking and signage elements related to the EV charging stations. Scope of Supply This shall include: - Vertical signage indicating EV charging points - Horizontal road/parking markings - Supporting elements for signage installation |  |  |  |
|  | Technical Requirements - Markings and signage shall: - Be clearly visible and durable - Comply with applicable local regulations The type and layout of signage and markings are defined in the technical documentation and graphic attachments. All traffic marking and signage elements shall be included in the Contractor’s scope of supply. *All the above activities are strictly limited to what is necessary for the installation and operation of the supplied EV charging system and shall not constitute standalone construction works. The Contractor shall determine all necessary materials and activities based on the technical documentation and include them in the financial offer. |  |  |  |

*Any reference in the Project documentation to specific brands, models, trade names, manufacturers or catalogue numbers is made solely for the purpose of indicating the expected level of quality, performance and functional requirements.

Such references shall be understood as followed by the words “or equivalent”.

Economic operators may propose equivalent solutions, provided that they demonstrate, to the satisfaction of the Contracting Authority, that the proposed equipment meets or exceeds the technical and performance requirements set out in these Technical Specifications.

*For all items and requirements specified in these Technical Specifications, equivalent solutions shall be accepted.